|  |  |
| --- | --- |
| Date |  |
| Location |  |
| Completed by |  |

| OK = Satisfactory | AN = Action Needed | N/A = Not Applicable | **OK** | **AN** | **N/A** |
| --- | --- | --- | --- |
| 1 | There is a fire protection program in place that is followed throughout all phases of the construction and demolition work. [1926.150(a)(1)] |[ ] [ ] [ ]
| 2 | Firefighting equipment is easy to find and readily accessible at all times. [1926.150(a)] |[ ] [ ] [ ]
| 3 | All firefighting equipment is periodically inspected and always maintained in safe operating condition. Defective equipment is immediately replaced. [1926.150(a)(4)] |[ ] [ ] [ ]
| 4 | A fire extinguisher, rated at least 2A, is provided for each 3,000 square feet of the protected building area. [1926.150(c)(1)(i)] |[ ] [ ] [ ]
| 5 | Travel distance from any point of the protected building area to the nearest fire extinguisher does not exceed 100 feet. [1926.150(c)(1)(i)] |[ ] [ ] [ ]
| 6 | A fire extinguisher, rated at least 2A, is provided on each floor and at least one fire extinguisher is by any stairways. [1926.150(c)(1)(iv)] |[ ] [ ] [ ]
| 7 | A fire extinguisher, rated at least 10B, is within 50 feet of where more than 5 gallons of flammable or combustible liquids or 5 lbs. of flammable gas are being used on the jobsite. [1926.150(c)(10(vi)] |[ ] [ ] [ ]
| 8 | If the facility being constructed includes the installation of automatic sprinkler protection, the installation closely follows the construction and is placed in service as soon as allowed. [1926.150(d)(1)(i)] |[ ] [ ] [ ]
| 9 | There is a fire alarm system that notifies employees on the jobsite and the local fire department in the event of an emergency. [1926.150(e)(1)] |[ ] [ ] [ ]
| 10 | Reporting instructions are posted at phones and at employee entrances. [1926.150(3)(2)] |[ ] [ ] [ ]
| 11 | Fire walls and exit stairways are given construction priority. Fire doors, with automatic closing devices, are hung on openings as soon as practicable. [1926.150(f)(1)] |[ ] [ ] [ ]
| **FIRE PREVENTION** |
| 12 | All solvent waste, oily rags, and flammable liquids shall be kept in fire resistant covered containers until removed from worksite. [1926.252(e)] |[ ] [ ] [ ]
| 13 | Internal combustion engine powered equipment is located where the exhausts are well away from combustible materials. When exhausts are piped to outside the building under construction, a clearance of at least 6 inches is maintained between the piping and any combustible material. [1926.151(a)(2)] |[ ] [ ] [ ]
| 14 | Smoking is prohibited near operations considered a fire hazard, and a sign is posted: "No Smoking or Open Flame." [1926.151(a)(3)] |[ ] [ ] [ ]
| 15 | Portable battery-powered lighting equipment, used with the storage, handling, or use of flammable gases or liquids, is of the type approved for the hazardous locations. [1926.151(a)(4)] |[ ] [ ] [ ]
| 16 | No temporary building has been erected where it adversely affects any means of exit. [1926.151(b)(1)] |[ ] [ ] [ ]
| 17 | Combustible materials are only piled in a stable manner and never piled higher than 20 feet. [1926.151(c)(1)] |[ ] [ ] [ ]
| 18 | The construction storage site does not have an accumulation of unnecessary combustible materials. Weeds and grass are kept down and there is a regular procedure for the periodic cleanup of the entire storage area. [1926.151(c)(3)] |[ ] [ ] [ ]
| 19 | There is no combustible material stored outdoors within 10 feet of a building or structure. [1926.151(c)(5)] |[ ] [ ] [ ]
| 20 | Indoor storage areas do not obstruct, or adversely affect, any means of exit. [1926.151(d)(1)] |[ ] [ ] [ ]
| 21 | There is a clearance of at least 36 inches between the top level of material stored indoors and the sprinkler heads. [1926.151(d)(5)] |[ ] [ ] [ ]
| 22 | Clearance is maintained around lights and heating units to prevent the ignition of combustible materials. [1926.151(d)(6)] |[ ] [ ] [ ]
| **FLAMMABLE LIQUIDS** |
| 23 | Only approved containers and portable tanks are used for storage and handling of flammable liquids. [1926.152(a)(1)] |[ ] [ ] [ ]
| 24 | Flammable liquids are not stored in areas used for exits, stairways, or passageways. [1926.152(a)(2)] |[ ] [ ] [ ]
| 25 | No more than 25 gallons of flammable liquids are stored in a room outside of an approved storage cabinet. [1926.152(b)(1)] |[ ] [ ] [ ]
| 26 | Quantities of flammable liquids greater than 25 gallons are stored in an acceptable or approved cabinet meeting the requirements of OSHA Standard 1926.152(b). |[ ] [ ] [ ]
| 27 | Cabinets storing flammable liquids are labeled "Flammable-Keep Away from Open Flames." [1926.152(b)(2)(iii)] |[ ] [ ] [ ]
| 28 | Flammable liquids stored outside in containers or tanks are at least 20 feet away from any building. [1926.152(c)] |[ ] [ ] [ ]
| 29 | Outdoor storage areas for flammable liquids are kept free of weeds, debris, and other combustible material. [1926.152(c)(5)] |[ ] [ ] [ ]
| 30 | At least one portable fire extinguisher, rated at least 20-B, is located outside of, but not more than 10 feet from, the door opening into any room used for storage of more than 60 gallons of flammable liquids. [1926.152(d)(1)] |[ ] [ ] [ ]
| 31 | At least one portable fire extinguisher, rated at least 20-B, is located between 25 – 75 feet from any flammable liquid storage area located outside. [1926.152(d)(2)] |[ ] [ ] [ ]
| 32 | At least one portable fire extinguisher rated at least 20-B:C is provided on all tank trucks or other vehicles used for transporting and/or dispensing flammable liquids. [1926.152(d)(4)] |[ ] [ ] [ ]
| 33 | Smoking and open flames are prohibited in areas used for fueling, servicing fuel systems, and receiving or dispensing flammable liquids. NO SMOKING signs are posted. [1926.152(g)(8-9)] |[ ] [ ] [ ]
| 34 | The motor of any equipment being fueled is shut off during the fueling operation. [1926.152(g)(10)] |[ ] [ ] [ ]
| 35 | Each service or fueling area has at least one fire extinguisher rated at least 20-B:C within 75 feet of each pump, dispenser, underground fill pipe opening, and lubrication or service area. [1926.152(g)(11)] |[ ] [ ] [ ]
| **LIQUIFIED PETROLEUM GAS (LPG)** |
| 36 | Welding on LPG containers is prohibited. [1926.153(b)] |[ ] [ ] [ ]
| 37 | LPG container safety relief devices and regulator relief vents are not located less than 5 feet in any direction from air openings into sealed combustion system appliances or mechanical ventilation air intakes. [1926.153(d)(3)] |[ ] [ ] [ ]
| 38 | LPG containers are not stored indoors. [1926.153(j)] |[ ] [ ] [ ]
| 39 | LPG containers are stored outside in a suitable ventilated enclosure that is protected against tampering. [1926.153(k)(2)] |[ ] [ ] [ ]
| 40 | LPG container storage locations have at least one approved portable fire extinguisher having a rating that is at least 20-B:C. [1926.153(l)] |[ ] [ ] [ ]
| 41 | LPG containers and systems are protected against possible damage from vehicular traffic. [1926.153(o)] |[ ] [ ] [ ]
| **WELDING AND CUTTING** |
| 42 | Objects to be welded, cut, or heated are moved to a designated location or movable fire hazards are taken to a safe place or otherwise protected. [1926.352(a)] |[ ] [ ] [ ]
| 43 | When the object to be welded cannot be moved and fire hazards cannot be removed, shields are used to confine heat, sparks, and slag. [1926.352(b)] |[ ] [ ] [ ]
| 44 | Suitable fire-extinguishing equipment is available for immediate use near welding operations. [1926.352(d)] |[ ] [ ] [ ]
| 45 | Fire watchers are assigned during welding operations when normal fire prevention precautions may not be sufficient. [1926.352(e)] |[ ] [ ] [ ]
| 46 | Oxygen cylinders in storage are separated from fuel gas cylinders and combustible materials (especially oil and grease) by at least 20 feet, or by a non-combustible barrier at least 5 feet high, having a fire-resistance rating of at least 30 minutes. [1926.350(a)(10)] |[ ] [ ] [ ]
| 47 | Cylinders are kept at a safe distance from welding operations, or fire-resistant shields provided. [1926.350(b)(1)] |[ ] [ ] [ ]
| 48 | Flashback protection is provided by an approved device that will prevent flame from passing into fuel-gas systems. |[ ] [ ] [ ]

|  |
| --- |
| Action Needed Items and Additional Notes: |
|  |

*This checklist provides general safety guidelines and does not include all elements of OSHA Standard 1926 Subpart F for Construction Fire Protection and Prevention.*

*This document may not be comprehensive for the requirements of the workforce or facility being evaluated. Weeklysafety.com does not assume liability for damage or injury presumed to be caused by use of this document. Use of this document does not guarantee conformity with any laws or regulations, nor does it ensure absolute workplace safety.*