|  |  |
| --- | --- |
| Date |  |
| Location |  |
| Completed by |  |

| OK = Satisfactory | AN = Action Needed | N/A = Not Applicable | **OK** | **AN** | **N/A** |
| --- | --- | --- | --- |
| 1 | All LPG equipment and systems have containers, valves, connectors, manifold valve assemblies, and regulators of an approved type. [1926.153(a)(1)] |[ ] [ ] [ ]
| 2 | Welding on LPG containers is prohibited. [1926.153(b)] |[ ] [ ] [ ]
| 3 | Valves, fittings, and accessories connected directly to any LPG container, including primary shut off valves, have a rated working pressure of at least 250 p.s.i.g. and are of material and design suitable for LPG service. [1926.153(c)(1)] |[ ] [ ] [ ]
| 4 | Connections to LPG containers, except safety relief connections, liquid level gauging devices, and plugged openings, have shutoff valves located as close to the container as practicable. [1926.153(c)(2)] |[ ] [ ] [ ]
| 5 | LPG container safety relief devices and regulator relief vents are not located less than 5 feet in any direction from air openings into sealed combustion system appliances or mechanical ventilation air intakes. [1926.153(d)(3)] |[ ] [ ] [ ]
| 6 | Filling of fuel containers for trucks or motor vehicles from bulk storage containers is performed more than 10 feet from the nearest masonry-walled building, or more than 25 feet from the nearest building or other construction and, in any event, more than 25 feet from any building opening. [1926.153(e)(1)] |[ ] [ ] [ ]
| 7 | Filling of portable LPG containers or containers mounted on skids from storage containers is performed more than 50 feet from the nearest building. [1926.153(e)(2)] |[ ] [ ] [ ]
| 8 | LPG containers and regulating equipment installed outside are upright on a firm foundation or otherwise firmly secured. [1926.153(g)] |[ ] [ ] [ ]
| 9 | When in use inside buildings or structures, LPG containers, regulating equipment, manifolds, pipe, tubing, and hose are located in an area to minimize exposure to high temperatures or physical damage. [1926.153(h)(10)] |[ ] [ ] [ ]
| 10 | LPG containers are not stored indoors. [1926.153(j)] |[ ] [ ] [ ]
| 11 | LPG containers stored outside are located away from the building as follows: [1926.153(k)(1)]* 500 lbs. or less – 0 feet
* 501 to 6,000 lbs. – 10 feet
* 6,001 – 10,000 lbs. – 20 feet
* Over 10,000 lbs. – 25 feet
 |[ ] [ ] [ ]
| 12 | LPG containers are stored outside in a suitable ventilated enclosure that is protected against tampering. [1926.153(k)(2)] |[ ] [ ] [ ]
| 13 | LPG container storage locations have at least one approved portable fire extinguisher having a rating that is at least 20-B:C. [1926.153(l)] |[ ] [ ] [ ]
| 14 | When LPG and one or more other gases are stored or used in the same area, the containers are marked to identify their contents. [1926.153(n)] |[ ] [ ] [ ]
| 15 | LPG containers and systems are protected against possible damage from vehicular traffic. [1926.153(o)] |[ ] [ ] [ ]

|  |
| --- |
| Action Needed Items and Additional Notes: |
|  |

*This document may not be comprehensive for the requirements of the workforce or facility being evaluated. Weeklysafety.com does not assume liability for damage or injury presumed to be caused by use of this document. Use of this document does not guarantee conformity with any laws or regulations, nor does it ensure absolute workplace safety.*